## Bridgeport Elementary
Location Number | Description | Sample # | Sample Date | Results | Remediation | Retest Sample # | Retest Date | Retest Results
1 | Kitchen Sink East Wall | BP-1 | 4/8/16 | .0082 mg/L
2 | Kitchen Sink Right North Wall | BP-2 | 4/8/16 | .0066 mg/L
3 | Kitchen Sink Center North Wall | BP-3 | 4/8/16 | .0075 mg/L
4 | Kitchen Sink Left North Wall | BP-4 | 4/8/16 | .0051 mg/L
5 | Kitchen Bath Hand Sink | BP2-5 | 9/28/16 | .022 mg/L | Posted Non-Potable, Replace fixture, Retest
6 | Kitchen Custodial Sink | BP2-6 | 9/28/16 | .033 mg/L | Posted Non-Potable, Replace fixture, Retest
7 | Room 125 Hand Sink | BP2-7 | 9/28/16 | .023 mg/L | Posted Non-Potable, Replace fixture, Retest
8 | Room 126 Hand Sink | BP2-8 | 9/28/16 | .0076 mg/L
9 | Main Entrance Water Fountain Right | BP-5 | 4/8/16 | .0036 mg/L
10 | Main Entrance Water Fountain Left | BP-6 | 4/8/16 | .0036 mg/L
11 | Boys Bath Hand Sink (Left) | BP2-11 | 9/28/16 | <.0010 mg/L
12 | Girls Bath Hand Sink (Right) | BP2-12 | 9/28/16 | <.0010 mg/L
13 | Main Office Hand Sink | BP-7 | 4/8/16 | .0030 mg/L
14 | Principal Bath Hand Sink | BP2-14 | 9/28/16 | .012 mg/L
15 | Room 102 Bath Hand Sink | BP2-15 | 9/28/16 | .0036 mg/L
16 | Room 102 Hand Sink | BP2-16 | 9/28/16 | .0038 mg/L
17 | Room 102 Water Fountain | BP-8 | 4/8/16 | .0026 mg/L
18 | Room 108 Nurses Office Hand Sink | BP-9 | 4/8/16 | .0043 mg/L
19 | Nurses Office Bath Hand Sink | BP2-19 | 9/28/16 | <.0010 mg/L
20 | Room 104 Bath Hand Sink | BP2-20 | 9/28/16 | .0054 mg/L
21 | Room 104 Hand Sink | BP2-21 | 9/28/16 | .0028 mg/L
22 | Room 104 Water Fountain | BP-10 | 4/8/16 | .0037 mg/L
23 | Fourth Grade Custodial Sink | BP2-23 | 9/28/16 | .0055 mg/L
24 | Room 103 Bath Hand Sink | BP2-24 | 9/28/16 | .0041 mg/L
25 | Room 103 Hand Sink | BP2-25 | 9/28/16 | .0032 mg/L
26 | Room 103 Water Fountain | BP-11 | 4/8/16 | .0040 mg/L
27 | Library Hand Sink | BP2-27 | 9/28/16 | .0045 mg/L
28 | Library Bath Hand Sink | BP2-28 | 9/28/16 | .0098 mg/L
29 | Library Hall Water Fountain | BP-12 | 4/8/16 | .005 mg/L
30 | Room 130 Bath Hand Sink | BP2-30 | 9/28/16 | .0049 mg/L
31 | Room 133 Bath Hand Sink | BP2-31 | 9/28/16 | .0032 mg/L
32 | Room 133 Counter Hand Sink(Hallway) | BP2-32 | 9/28/16 | .0010 mg/L
33 | Room 133 Counter Hand Sink (Window) | BP2-33 | 9/28/16 | <.0010 mg/L
34 | Room 122/105 Bath Hand Sink | BP2-34 | 9/28/16 | .020 mg/L | Posted Non-Potable, Replace fixture, Retest
35 | Room 105 Water Fountain | BP-14 | 4/8/16 | .0028 mg/L
36 | Room 105 Hand Sink | BP2-36 | 9/28/16 | .0039 mg/L
37 | Room 105/106 Bath Hand Sink | BP2-37 | 9/28/16 | .0038 mg/L
38 | Room 134 Water Fountain | BP-13 | 4/8/16 | .0030 mg/L
39 | Room 134 Hand Sink | BP2-39 | 9/28/16 | .0037 mg/L
40 | Room 134/107 Bath Hand Sink | BP2-40 | 9/28/16 | .0041 mg/L
41 | Room 107 Water Fountain | BP-15 | 4/8/16 | .0049 mg/L
42 | Room 107 Hand Sink | BP2-42 | 9/28/16 | .014 mg/L
43 | Room 107 Bath Hand Sink | BP2-43 | 9/28/16 | .024 mg/L | Posted Non-Potable, Replace fixture, Retest
44 | Room 106 Water Fountain | BP-16 | 4/8/16 | .0042 mg/L
45 | Room 106 Hand Sink | BP2-45 | 9/28/16 | .026 mg/L | Posted Non-Potable, Replace fixture, Retest
46 | Room 106 Bath Hand Sink | BP2-46 | 9/28/16 | .0040 mg/L
47 | Room 113 Hand Sink | BP2-47 | 9/28/16 | .0016 mg/L
48 | Room 113 Water Fountain | BP-22 | 4/8/16 | .0043 mg/L
49 | Room 114 Hand Sink | BP2-49 | 9/28/16 | .0012 mg/L
50 | Room 114 Water Fountain | BP-20 | 4/8/16 | .0017 mg/L
51 | Room 101 Hand Sink | BP-18 | 4/8/16 | .0013 mg/L
52 | Room 101 Bath Hand Sink | BP2-52 | 9/28/16 | .0018 mg/L
53 | Room 120 Bath Hand Sink | BP2-53 | 9/28/16 | .0036 mg/L
54 | Room 120 Hand Sink | BP2-54 | 9/28/16 | .0080 mg/L
55 | Room 120 Water Fountain | BP-17 | 4/8/16 | .0031 mg/L
56 | Room 121 Water Fountain | BP-19 | 4/8/16 | <.0010 mg/L
57 | Room 121 Hand Sink | BP2-57 | 9/28/16 | <.0010 mg/L
58 | Room 128 Hand Sink | BP2-58 | 9/28/16 | <.0010 mg/L
59 | Room 128 Water Fountain | BP-21 | 4/8/16 | .0038 mg/L
60 | Room 119 Water Fountain | BP-23 | 4/8/16 | <.0010 mg/L
61 | Room 119 Hand Sink | BP2-61 | 9/28/16 | .015 mg/L | Posted Non-Potable, Replace fixture, Retest
62 | Room 112 Hand Sink | BP2-62 | 9/28/16 | .0011 mg/L
63 | Room 112 Water Fountain | BP-25 | 4/8/16 | .0031 mg/L
64 | Room 118 Water Fountain | BP-24 | 4/8/16 | .0014 mg/L
65 | Room 118 Hand Sink | BP2-65 | 9/28/16 | .0012 mg/L
66 | Room 117 Water Fountain | BP-26 | 4/8/16 | .0021 mg/L
67 | Room 117 Hand Sink | BP2-67 | 9/28/16 | .0011 mg/L
68 | Room 111 Hand Sink | BP2-68 | 9/28/16 | .0079 mg/L
69 | Room 111 Water Fountain | BP-27 | 4/8/16 | .0030 mg/L
70 | Room 116 Water Fountain | BP-28 | 4/8/16 | <.0010 mg/L
71 | Room 116 Hand Sink | BP2-71 | 9/28/16 | .0027 mg/L
72 | Room 110 Hand Sink | BP2-72 | 9/28/16 | .0054 mg/L
73 | Room 110 Hot Water Supply | BP-29 | 4/8/16 | .0068 mg/L
74 | Room 123 Hand Sink | BP2-74 | 9/28/16 | .0084 mg/L
75 | Gym Hall Water Fountain | BP-31 | 4/8/16 | .0040 mg/L
76 | Room 115 Hand Sink | BP2-76 | 9/28/16 | .014 mg/L
77 | Room 115 Water Fountain | BP-32 | 4/8/16 | .0040 mg/L
78 | Boys Locker Left Hand Sink | BP2-78 | 9/28/16 | .018 mg/L | Posted Non-Potable, Replace fixture, Retest
79 | Boys Locker Right Hand Sink | BP2-79 | 9/28/16 | .0045 mg/L
80 | Boys Locker Water Fountain | BP-33 | 4/8/16 | .024 mg/L | Disconnected power and water supply to fountain. No longer in service.
81 | PE Office Hand Sink | BP2-81 | 9/28/16 | .010 mg/L
82 | Room 109 Left Water Fountain | BP-35 | 4/8/16 | .0058 mg/L
83 | Room 109 Hand Sink (Center) | BP2-83 | 9/28/16 | .0016 mg/L
84 | Room 109 Right Water Fountain | BP-30 | 4/8/16 | <.0010 mg/L
85 | Room 109 Hand Sink (Right) | BP2-85 | 9/28/16 | .0036 mg/L
86 | Custodial Closet Sink | BP2-86 | 9/28/16 | .0021 mg/L
87 | Girls Locker Left Hand Sink | BP2-87 | 9/28/16 | .0077 mg/L
88 | Girls Locker Right Hand Sink | BP2-88 | 9/28/16 | .018 mg/L | Posted Non-Potable, Replace fixture, Retest
89 | Girls Locker Water Fountain | BP-34 | 4/8/16 | .014 mg/L | Disconnected power and water supply to fountain. No longer in service.
90 | Maint Office Custodial Sink | BP2-90 | 9/28/16 | .0043 mg/L

## Bolivar Elementary
Location Number | Description | Sample # | Sample Date | Results | Remediation | Retest Sample # | Retest Date | Retest Results
1 | Kitchen Wash Sink Left/North Wall | BO-4 | 4/8/16 | <.0010 mg/L
2 | Kitchen Wash Sink Center/North Wall | BO-3 | 4/8/16 | <.0010 mg/L
3 | Kitchen Wash Sink Right/North Wall | BO-2 | 4/8/16 | <.0010 mg/L
4 | Kitchen Wash Sink East Wall | BO-1 | 4/8/16 | .0014 mg/L
5 | Soup Kettle Supply | BO-5 | 4/8/16 | .0012 mg/L
6 | Kitchen Bath Hand Sink | BO2-6 | 9/29/16 | <.0010 mg/L
7 | Faculty Hand Sink | BO-6 | 4/8/16 | <.0010 mg/L
8 | Faculty Bath Hand Sink | BO2-8 | 9/29/16 | <.0010 mg/L
9 | Library Hand Sink | BO-7 | 4/8/16 | .0015 mg/L
10 | Library Hall Custodial Sink | BO2-100 | 9/29/16 | .13 mg/L | Posted Non-Potable, Replace fixture, Retest
11 | Room 176 Water Fountain | BO-8 | 4/8/16 | <.0010 mg/L
12 | Room 176 Hand Sink | BO2-12 | 9/29/16 | <.0010 mg/L
13 | Room 171 South Wall Hand Sink | BO2-13 | 9/29/16 | <.0010 mg/L
14 | Room 171 Island Hand Sink (Hall) | BO2-14 | 9/29/16 | .0040 mg/L
15 | Room 171 Island Hand Sink (Window) | BO2-15 | 9/29/16 | .0051 mg/L
16 | Room 170 Hand Sink | BO2-16 | 9/29/16 | <.0010 mg/L
17 | Room 170 Water Fountain | BO-9 | 4/8/16 | <.0010 mg/L
18 | Room 114 Water Fountain | BO-10 | 4/8/16 | <.0010 mg/L
19 | Room 114 Hand Sink | BO2-19 | 9/29/16 | <.0010 mg/L
20 | Room 115 Hand Sink | BO2-20 | 9/29/16 | <.0010 mg/L
21 | Room 115 Water Fountain | BO-11 | 4/8/16 | <.0010 mg/L
22 | Second Grade Hall Custodial Sink | BO2-22 | 9/29/16 | .0052 mg/L
23 | Room 132 Water Fountain | BO-12 | 4/8/16 | <.0010 mg/L
24 | Room 132 Hand Sink | BO2-24 | 9/29/16 | <.0010 mg/L
25 | Room 131 Water Fountain | BO-13 | 4/8/16 | <.0010 mg/L
26 | Room 131 Hand Sink | BO2-26 | 9/29/16 | <.0010 mg/L
27 | Room 130 Water Fountain | BO-14 | 4/8/16 | <.0010 mg/L
28 | Room 130 Hand Sink | BO2-28 | 9/29/16 | <.0010 mg/L
29 | Room 129 Water Fountain | BO-15 | 4/8/16 | <.0010 mg/L
30 | Room 129 Hand Sink | BO2-30 | 9/29/16 | .0078 mg/L
31 | Room 128 Water Fountain | BO-16 | 4/8/16 | <.0010 mg/L
32 | Room 128 Hand Sink | BO2-32 | 9/29/16 | <.0010 mg/L
33 | Room 127 Water Fountain | BO-17 | 4/8/16 | <.0010 mg/L
34 | Room 127 Hand Sink | BO2-34 | 9/29/16 | <.0010 mg/L
35 | Room 126 Water Fountain | BO-18 | 4/8/16 | <.0010 mg/L
36 | Room 126 Hand Sink | BO2-36 | 9/29/16 | <.0010 mg/L
37 | Room 125 Water Fountain | BO-19 | 4/8/16 | <.0010 mg/L
38 | Room 125 Hand Sink | BO2-38 | 9/29/16 | <.0010 mg/L
39 | Room 122 Hand Sink | BO2-39 | 9/29/16 | .0018 mg/L
40 | Room 122 Water Fountain | BO-21 | 4/8/16 | <.0010 mg/L
41 | Room 121 Water Fountain | BO-20 | 4/8/16 | <.0010 mg/L
42 | Room 121 Hand Sink | BO2-42 | 9/29/16 | .0014 mg/L
43 | Room 119 Water Fountain | BO-22 | 4/8/16 | <.0010 mg/L
44 | Room 119 Hand Sink | BO2-44 | 9/29/16 | <.0010 mg/L
45 | Room 120 Hand Sink | BO2-45 | 9/29/16 | .0014 mg/L
46 | Room 120 Water Fountain | BO-23 | 4/8/16 | <.0010 mg/L
47 | Room 116 Water Fountain | BO-24 | 4/8/16 | <.0010 mg/L
48 | Room 116 Hand Sink | BO2-48 | 9/29/16 | .0010 mg/L
49 | Room 118 Hand Sink | BO2-49 | 9/29/16 | <.0010 mg/L
50 | Room 118 Water Fountain | BO-25 | 4/8/16 | <.0010 mg/L
51 | Receiving Room Custodial Sink | BO2-51 | 9/29/16 | <.0010 mg/L
52 | Room 134 Hand Sink | BO2-52 | 9/29/16 | .0026 mg/L
53 | Cafeteria Bath Hand Sink | BO2-53 | 9/29/16 | .0037 mg/L
54 | Cafeteria Water Fountain Right | BO-30 | 4/8/16 | <.0010 mg/L
55 | Cafeteria Water Fountain Left | BO-31 | 4/8/16 | <.0010 mg/L
56 | Girls Bathroom Left Hand Sink | BO2-56 | 9/29/16 | <.0010 mg/L
57 | Girls Bathroom Center Hand Sink | BO2-57 | 9/29/16 | <.0010 mg/L
58 | Girls Bathroom Right Hand Sink | BO2-58 | 9/29/16 | <.0010 mg/L
59 | Boys Bathroom Right Hand Sink | BO2-59 | 9/29/16 | <.0010 mg/L
60 | Boys Bathroom Center Hand Sink | BO2-60 | 9/29/16 | <.0010 mg/L
61 | Boys Bathroom Left Hand Sink | BO2-61 | 9/29/16 | <.0010 mg/L
62 | Main Entrance Water Fountain | BO-32 | 4/8/16 | <.0010 mg/L
63 | Main Office Hand Sink | BO-33 | 4/8/16 | <.0010 mg/L
64 | Main Office Hall Bath Hand Sink | BO2-64 | 9/29/16 | <.0010 mg/L
65 | Nurses Office Hand Sink | BO-34 | 4/8/16 | <.0010 mg/L
66 | Nurses Office Bath Hand Sink | BO2-66 | 9/29/16 | <.0010 mg/L
67 | Kindergarten/First Hall Water Fountain | BO-35 | 4/8/16 | <.0010 mg/L
68 | Coaches Office Bath Hand Sink | BO2-68 | 9/29/16 | .0019 mg/L
69 | Kindergarten Hall Bath Hand Sink | BO2-69 | 9/29/16 | .0012 mg/L
70 | Kindergarten Hall Custodial Sink | BO2-70 | 9/29/16 | .0032 mh/L
71 | Room 100 Hand Sink | BO2-71 | 9/29/16 | <.0010 mg/L
72 | Room 100 Water Fountain | BO-38 | 4/8/16 | <.0010 mg/L
73 | Room 101 Hand Sink | BO2-73 | 9/29/16 | <.0010 mg/L
74 | Room 104 Water Fountain | BO-39 | 4/8/16 | <.0010 mg/L
75 | Room 104 Hand Sink | BO2-75 | 9/29/16 | <.0010 mg/L
76 | Room 103 Hand Sink | BO2-76 | 9/29/16 | .0014 mg/L
77 | Room 103 Water Fountain | BO-40 | 4/8/16 | <.0010 mg/L
78 | Room 106 Water Fountain | BO-41 | 4/8/16 | <.0010 mg/L
79 | Room 106 Hand Sink | BO2-79 | 9/29/16 | <.0010 mg/L
80 | Room 105 Hand Sink | BO2-80 | 9/29/16 | .0012 mg/L
81 | Room 105 Water Fountain | BO-42 | 4/8/16 | <.0010 mg/L
82 | Room 108 Hand Sink Right | BO-43 | 4/8/16 | <.0010 mg/L
83 | Room 108 Hand Sink Left | BO-44 | 4/8/16 | <.0010 mg/L
84 | Rom 107 Hand Sink | BO2-84 | 9/29/16 | .0027 mg/L
85 | Room 107 Water Fountain | BO-45 | 4/8/16 | <.0010 mg/L
86 | Room 110 Hand Sink Left | BO-47 | 4/8/16 | .0023 mg/L
87 | Room 110 Hand Sink Right | BO-46 | 4/8/16 | <.0010 mg/L
88 | Room 109 Hand Sink Left | BO-49 | 4/8/16 | .0011 mg/L
89 | Room 109 Hand Sink Right | BO-48 | 4/8/16 | .0015 mg/L
90 | Room 112 Hand Sink Right | BO-51 | 4/8/16 | .0011 mg/L
91 | Room 112 Hand Sink Left | BO-52 | 4/8/16 | .0033 mg/L
92 | Room 111 Hand Sink Right | BO-53 | 4/8/16 | .0013 mg/L
93 | Room 111 Hand Sink Left | BO-54 | 4/8/16 | .0012 mg/L
94 | Kindergarten Hall Water Fountain | BO-50 | 4/8/16 | <.0010 mg/L
95 | Multipurpose Hall Water Fountain Right | BO-36 | 4/8/16 | <.0010 mg/L
96 | Multipurpose Hall Water Fountain Left | BO-37 | 4/8/16 | <.0010 mg/L
97 | Boys Bathroom Hand Sink | BO2-97 | 9/29/16 | <.0010 mg/L
98 | Girls Bathroom Hand Sink | BO2-98 | 9/29/16 | <.0010 mg/L
99 | Coaches Office Bath Hand Sink | BO2-99 | 9/29/16 | .0024 mg/L
100 | Receiving Area Outside Hose Bib | BO2-100 | 9/29/16 | .0035 mg/L

## Middle School
Location Number | Description | Sample # | Sample Date | Results | Remediation | Retest Sample # | Retest Date | Retest Results
1 | Kitchen Custodial Sink | MS2-1 | 9/27/16 | .0013 mg/L
2 | Ice Maker | MS2-2 | 9/27/16 | .014 mg/L
3 | Kitchen Hand Sink | MS-32 | 4/12/16 | .0012 mg/L
4 | Cook Sink North | MS-1 | 4/12/16 | .0027 mg/L
5 | Cook Sink South | MS-2 | 4/12/16 | .0025 mg/L
6 | Cook Sink Left | MS-5 | 4/12/16 | .0017 mg/L
7 | Cook Sink Right | MS-6 | 4/12/16 | .0024 mg/L
8 | Kettle Nearest Office | MS-3 | 4/12/16 | .0027 mg/L
9 | Kettle Nearest Dishwasher | MS-4 | 4/12/16 | <.0010 mg/L
10 | Cook Sink (Island) | MS-7 | 4/12/16 | .0023 mg/L
11 | Kitchen Hand Sink | MS-8 | 4/12/16 | <.0010 mg/L
12 | Food Service Bath Hand Sink | MS2-12 | 9/27/16 | <.0010 mg/L
13 | Faculty Room Sink | MS-10 | 4/12/16 | .0011 mg/L
14 | Cafeteria Water Fountain | MS-9 | 4/12/16 | <.0010 mg/L
15 | Boys Bath Hand Sink Left | MS2-15 | 9/27/16 | .0013 mg/L
16 | Boys Bath Hand Sink Right | MS2-16 | 9/27/16 | .0024 mg/L
17 | Girls Bath Hand Sink Left | MS2-17 | 9/27/16 | .0016 mg/L
18 | Girls Bath Hand Sink Right | MS2-18 | 9/27/16 | <.0010 mg/L
19 | Cafeteria Hall Water Fountain | MS-11 | 4/12/16 | <.0010 mg/L
20 | Womens Bath Hand Sink | MS2-20 | 9/27/16 | .0023 mg/L
21 | Mens Bath Hand Sink | MS2-21 | 9/27/16 | .0026 mg/L
22 | Band Practice Room Hand Sink | MS2-22 | 9/27/16 | .0011 mg/L
23 | Gym Hall Water Fountain North | MS-12 | 4/12/16 | <.0010 mg/L
24 | Boys Locker Hand Sink Right | MS2-24 | 9/27/16 | <.0010 mg/L
25 | Boys Locker Hand Sink Left | MS2-25 | 9/27/16 | .0039 mg/L
26 | Mens PE Office Bath Hand Sink | MS2-26 | 9/27/16 | .0011 mg/L
27 | Gym Custodial Sink | MS2-27 | 9/27/16 | .0024 mg/L
28 | Gym Hall Water Fountain South | MS-13 | 4/12/16 | <.0010 mg/L
29 | Girls Locker Hand Sink Left | MS2-29 | 9/27/16 | .0019 mg/L
30 | Girls Locker Hand Sink Right | MS2-30 | 9/27/16 | <.0010 mg/L
31 | Womens PE Office Bath Hand Sink | MS2-31 | 9/27/16 | .0014 mg/L
32 | Room 114 Hand Sink North | MS-17 | 4/12/16 | .019 mg/L | Replaced Faucet, Supply Lines, fittings, and solder to main | 10/4/2016 | MS3-32 | .0061 mg/L
33 | Room 114 Hand Sink Right | MS-14 | 4/12/16 | .0039 mg/L
34 | Room 114 Hand Sink Left | MS-15 | 4/12/16 | .0049 mg/L
35 | Room 114 Hand Sink East | MS-16 | 4/12/16 | .0019 mg/L
36 | Room 113 Hand Sink West | MS-20 | 4/12/16 | .0015 mg/L
37 | Room 113 Hand Sink Right | MS-19 | 4/12/16 | .0028 mg/L
38 | Room 113 Hand Sink Left | MS-18 | 4/12/16 | .0017 mg/L
39 | Room 113 Hand Sink North | MS-21 | 4/12/16 | .0027 mg/L
40 | Room 116 Hand Sink North | MS2-40 | 9/27/16 | .0067 mg/L
41 | Room 116 Island Hand Sink North | MS2-41 | 9/27/16 | .0099 mg/L
42 | Room 116 Island Hand Sink South | MS2-42 | 9/27/16 | .0027 mg/L
43 | Room 117 Island Hand Sink South | MS2-43 | 9/27/16 | .0037 mg/L
44 | Room 117 Island Hand Sink North | MS2-44 | 9/27/16 | .0026 mg/L
45 | Room 117 Hand Sink North | MS2-45 | 9/27/16 | .0028 mg/L
46 | Board Room (small) Bath Hand Sink | MS2-46 | 9/27/16 | .0045 mg/L
47 | Board Room (large) Bath Hand Sink | MS2-47 | 9/27/16 | .0061 mg/L
48 | Board Room Hand Sink | MS-31 | 4/12/16 | .0014 mg/L
49 | Special Needs Break Room Hand Sink | MS-30 | 4/12/16 | .0011 mg/L
50 | District Office Bath Hand Sink | MS2-50 | 9/27/16 | .012 mg/L
51 | Womens Bath Hand Sink | MS2-51 | 9/27/16 | .0046 mg/L
52 | District Office Break Room Sink | MS-29 | 4/12/16 | <.0010 mg/L
53 | Supt Office Bath Hand Sink | MS2-53 | 9/27/16 | .0063 mg/L
54 | District Office Custodial Sink | MS2-54 | 9/27/16 | .012 mg/L
55 | Nurses Office Bath Hand Sink South | MS2-55 | 9/27/16 | .0029 mg/L
56 | Nurses Office Hand Sink | MS-28 | 4/12/16 | .0012 mg/L
57 | Nurses Office Bath Hand Sink North | MS2-57 | 9/27/16 | .0073 mg/L
58 | Main Office Bath Hand Sink | MS-27 | 4/12/16 | <.0010 mg/L
59 | Library Hand Sink | MS-26 | 4/12/16 | <.0010 mg/L
60 | Pod A Hall Water Fountain | MS-25 | 4/12/16 | <.0010 mg/L
61 | Pod A Boys Bath Hand Sink Right | MS2-61 | 9/27/16 | <.0010 mg/L
62 | Pod A Boys Bath Hand Sink Left | MS2-62 | 9/27/16 | .0020 mg/L
63 | Pod A Girls Bath Hand Sink Left | MS2-63 | 9/27/16 | <.0010 mg/L
64 | Pod A Girls Bath Hand Sink Right | MS2-64 | 9/27/16 | <.0010 mg/L
65 | Pod A Custodial Sink | MS2-65 | 9/27/16 | <.0010 mg/L
66 | Room 103 Bath Hand Sink | MS2-66 | 9/27/16 | .0014 mg/L
67 | Room 103/104 Hand Sink | MS2-67 | 9/27/16 | .0028 mg/L
68 | Science Hall Water Fountain | MS-24 | 4/12/16 | <.0010 mg/L
69 | Room 137 Island Sink (Inside of Room) | MS2-69 | 9/27/16 | .012 mg/L
70 | Room 137 Island Sink (Outside Wall) | MS2-70 | 9/27/16 | .034 mg/L | Posted Non-Potable, Replace fixture, Retest
71 | Room 137 Island Sink (Inside of Room) | MS2-71 | 9/27/16 | .051 mg/L | Posted Non-Potable, Replace fixture, Retest
72 | Room 137 Island Sink (Outside Wall) | MS2-72 | 9/27/16 | .036 mg/L | Posted Non-Potable, Replace fixture, Retest
73 | Room 137 Island Sink (Inside of Room) | MS2-73 | 9/27/16 | .016 mg/L | Posted Non-Potable, Replace fixture, Retest
74 | Room 137 Island Sink (Outside Wall) | MS2-74 | 9/27/16 | .021 mg/L | Posted Non-Potable, Replace fixture, Retest
75 | Room 137 Island Sink (Inside of Room) | MS2-75 | 9/27/16 | .014 mg/L
76 | Room 137 Island Sink (Outside Wall) | MS2-76 | 9/27/16 | .022 mg/L | Posted Non-Potable, Replace fixture, Retest
77 | Room 137 Island Sink (Inside of Room) | MS2-77 | 9/27/16 | .47 mg/L | Posted Non-Potable, Replace fixture, Retest
78 | Room 137 Island Sink (Outside Wall) | MS2-78 | 9/27/16 | 1.2 mg/L | Posted Non-Potable, Replace fixture, Retest
79 | Room 137 Island Sink (Inside of Room) | MS2-79 | 9/27/16 | .012 mg/L
80 | Room 137 Island Sink (Outside Wall) | MS2-80 | 9/27/16 | .077 mg/L | Posted Non-Potable, Replace fixture, Retest
81 | Room 137 Island Hand Sink (teacher) | MS2-81 | 9/27/16 | .0092 mg/L
82 | Room 137/138 Storage Hand Sink | MS2-82 | 9/27/16 | .010 mg/L
83 | Room 138 Island Hand Sink (teacher) | MS2-83 | 9/27/16 | .0099 mg/L
84 | Room 138 Island Sink (Outside Wall) | MS2-84 | 9/27/16 | .011 mg/L
85 | Room 138 Island Sink (Inside of Room) | MS2-85 | 9/27/16 | .015 mg/L | Posted Non-Potable, Replace fixture, Retest
86 | Room 138 Island Sink (Outside Wall) | MS2-86 | 9/27/16 | .012 mg/L
87 | Room 138 Island Sink (Inside of Room) | MS2-87 | 9/27/16 | .012 mg/L
88 | Room 138 Island Sink (Inside of Room) | MS2-88 | 9/27/16 | .022 mg/L | Posted Non-Potable, Replace fixture, Retest
89 | Room 138 Island Sink (Outside Wall) | MS2-89 | 9/27/16 | .0094 mg/L
90 | Room 138 Island Sink (Inside of Room) | MS2-90 | 9/27/16 | .0053 mg/L
91 | Room 138 Island Sink (Outside Wall) | MS2-91 | 9/27/16 | .015 mg/L | Posted Non-Potable, Replace fixture, Retest
92 | Room 138 Island Sink (Inside of Room) | MS2-92 | 9/27/16 | .0071 mg/L
93 | Room 138 Island Sink (Outside Wall) | MS2-93 | 9/27/16 | .011 mg/L
94 | Room 138 Island Sink (Inside of Room) | MS2-94 | 9/27/16 | .016 mg/L | Posted Non-Potable, Replace fixture, Retest
95 | Room 138 Island Sink (Outside Wall) | MS2-95 | 9/27/16 | .38 mg/L | Posted Non-Potable, Replace fixture, Retest
96 | Greenhouse Hand Sink (Inside of Room) | MS2-96 | 9/27/16 | .011 mg/L
97 | Greenhouse Hose Bib | MS2-97 | 9/27/16 | .0026 mg/L
98 | Maintenance Break Hand Sink | MS-23 | 4/12/16 | <.0010 mg/L
99 | Maintenance Bath Hand Sink | MS2-99 | 9/27/16 | .0020 mg/L
100 | Pod B Hall Water Fountain | MS-22 | 4/12/16 | <.0010 mg/L
101 | Pod B Girls Bath Hand Sink Left | MS2-101 | 9/27/16 | .0030 mg/L
102 | Pod B Girls Bath Hand Sink Right | MS2-102 | 9/27/16 | .0020 mg/L
103 | Pod B Boys Bath Hand Sink Right | MS2-103 | 9/27/16 | .0060 mg/L
104 | Pod B Boys Bath Hand Sink Left | MS2-104 | 9/27/16 | .0064 mg/L
105 | Pod B Custodial Sink | MS2-105 | 9/27/16 | .0022 mg/L
106 | Room 111 Hand Sink | MS2-106 | 9/27/16 | .0054 mg/L
107 | Room 111 Classroom Hand Sink | MS2-107 | 9/27/16 | .0083 mg/L
108 | Room 112 Hand Sink | MS2-108 | 9/27/16 | .0087 mg/L
109 | Pod C Outside Hose Bib | MS2-109 | 9/27/16 | .0035 mg/L
110 | Room 212 Storage Hand Sink | MS2-110 | 9/27/16 | .0018 mg/L
111 | Room 211 Storage Hand Sink | MS2-111 | 9/27/16 | .0049 mg/L
112 | Pod B 2nd Floor Water Fountain | MS-34 | 4/12/16 | <.0010 mg/L
113 | Pod B Boys Bath Hand Sink Right | MS2-113 | 9/27/16 | <.0010 mg/L
114 | Pod B Boys Bath Hand Sink Left | MS2-114 | 9/27/16 | .0014 mg/L
115 | Pod B Girls Bath Hand Sink Left | MS2-115 | 9/27/16 | <.0010 mg/L
116 | Pod B Girls Bath Hand Sink Right | MS2-116 | 9/27/16 | .0015 mg/L
117 | Pod B 2nd Floor Custodial Sink | MS2-117 | 9/27/16 | .0018 mg/L
118 | Room 213 Hand Sink Left | MS2-118 | 9/27/16 | .0078 mg/L
119 | Room 213 Hand Sink Right | MS2-119 | 9/27/16 | .0040 mg/L
120 | Room 214 Hand Sink Right | MS2-120 | 9/27/16 | .0080 mg/L
121 | Room 214 Hand Sink Left | MS2-121 | 9/27/16 | .14 mg/L | Posted Non-Potable, Replace fixture, Retest
122 | 61 Wing Water Fountain | MS-33 | 4/12/16 | .0040 mg/L
123 | Faculty Bath Hand Sink | MS2-123 | 9/27/16 | .0011 mg/L
124 | Faculty Break Room Hand Sink | MS-35 | 4/12/16 | .0017 mg/L
125 | Room 225 Island Sink (Outside Wall) | MS2-125 | 9/27/16 | .0065 mg/L
126 | Room 225 Island Sink (Inside of Room) | MS2-126 | 9/27/16 | .012 mg/L
127 | Room 225 Island Sink (Outside Wall) | MS2-127 | 9/27/16 | .0088 mg/L
128 | Room 225 Island Sink (Inside of Room) | MS2-128 | 9/27/16 | .011 mg/L
129 | Room 225 Island Sink (Outside Wall) | MS2-129 | 9/27/16 | .010 mg/L
130 | Room 225 Island Sink (Inside of Room) | MS2-130 | 9/27/16 | .013 mg/L
131 | Room 225 Island Sink (Outside Wall) | MS2-131 | 9/27/16 | .015 mg/L | Posted Non-Potable, Replace fixture, Retest
132 | Room 225 Island Sink (Inside of Room) | MS2-132 | 9/27/16 | .014 mg/L
133 | Room 225 Island Sink (Outside Wall) | MS2-133 | 9/27/16 | .0077 mg/L
134 | Room 225 Island Sink (Inside of Room) | MS2-134 | 9/27/16 | .0099 mg/L
135 | Room 225 Island Sink (Outside Wall) | MS2-135 | 9/27/16 | .0061 mg/L
136 | Room 225 Island Sink (Inside of Room) | MS2-136 | 9/27/16 | .0089 mg/L
137 | Room 225 Hand Sink (teacher) | MS2-137 | 9/27/16 | .018 mg/L | Posted Non-Potable, Replace fixture, Retest
138 | Room 225/224 Storage Hand Sink | MS2-138 | 9/27/16 | .025 mg/L | Posted Non-Potable, Replace fixture, Retest
139 | Room 224 Hand Sink (teacher) | MS2-139 | 9/27/16 | .023 mg/L | Posted Non-Potable, Replace fixture, Retest
140 | Room 224 Island Sink (Inside of Room) | MS2-140 | 9/27/16 | .026 mg/L | Posted Non-Potable, Replace fixture, Retest
141 | Room 224 Island Sink (Outside Wall) | MS2-141 | 9/27/16 | .054 mg/L | Posted Non-Potable, Replace fixture, Retest
142 | Room 224 Island Sink (Inside of Room) | MS2-142 | 9/27/16 | .085 mg/L | Posted Non-Potable, Replace fixture, Retest
143 | Room 224 Island Sink (Outside Wall | MS2-143 | 9/27/16 | .045 mg/L | Posted Non-Potable, Replace fixture, Retest
144 | Room 224 Island Sink (Inside of Room) | MS2-144 | 9/27/16 | .030 mg/L | Posted Non-Potable, Replace fixture, Retest
145 | Room 224 Island Sink (Outside Wall | MS2-145 | 9/27/16 | .021 mg/L | Posted Non-Potable, Replace fixture, Retest
146 | Room 224 Island Sink (Inside of Room) | MS2-146 | 9/27/16 | .022 mg/L | Posted Non-Potable, Replace fixture, Retest
147 | Room 224 Island Sink (Outside Wall | MS2-147 | 9/27/16 | .022 mg/L | Posted Non-Potable, Replace fixture, Retest
148 | Room 224 Island Sink (Inside of Room) | MS2-148 | 9/27/16 | .025 mg/L | Posted Non-Potable, Replace fixture, Retest
149 | Room 224 Island Sink (Outside Wall | MS2-149 | 9/27/16 | .022 mg/L | Posted Non-Potable, Replace fixture, Retest
150 | Room 224 Island Sink (Inside of Room) | MS2-150 | 9/27/16 | .011 mg/L
151 | Room 224 Island Sink (Outside Wall | MS2-151 | 9/27/16 | .017 mg/L | Posted Non-Potable, Replace fixture, Retest
152 | 2nd Floor Science Wing Water Fountain | MS-36 | 4/12/16 | <.0010 mg/L
153 | Pod A 2nd Floor Water Fountain | MS-37 | 4/12/16 | <.0010 mg/L
154 | Pod A Boys Bath Hand Sink Right | MS2-154 | 9/27/16 | <.0010 mg/L
155 | Pod A Boys Bath Hand Sink Left | MS2-155 | 9/27/16 | .0015 mg/L
156 | Pod A Girls Bath Hand Sink Left | MS2-156 | 9/27/16 | <.0010 mg/L
157 | Pod A Girls Bath Hand Sink Right | MS2-157 | 9/27/16 | .0019 mg/L
158 | Pod A 2nd Floor Custodial Sink | MS2-158 | 9/27/16 | .0033 mg/L
159 | Room 204 Hand Sink Right | MS2-159 | 9/27/16 | .0031 mg/L
160 | Room 204 Hand Sink Left | MS2-160 | 9/27/16 | .0078 mg/L
161 | Room 203 Hand Sink Left | MS2-161 | 9/27/16 | .013 mg/L
162 | Room 203 Hand Sink Right | MS2-162 | 9/27/16 | .0025 mg/L

## High School
Location Number | Description | Sample # | Sample Date | Results | Remediation | Retest Sample # | Retest Date | Retest Results
1 | Room 113 Hand Sink | HS2-1 | 10/25/2016 | .0079 mg/L
2 | Receiving Hall Custodial Sink | HS2-2 | 10/25/2016 | .083 mg/L | Posted Non-Potable, Replace fixture, Retest
3 | Room 114 South Island Sink West | HS2-3 | 10/25/2016 | .010 mg/L
4 | Room 114 South Island Sink | HS2-4 | 10/25/2016 | .015 mg/L | Posted Non-Potable, Replace fixture, Retest
5 | Room 114 South Island Sink | HS2-5 | 10/25/2016 | .013 mg/L
6 | Room 114 South Island Sink East | HS2-6 | 10/25/2016 | .013 mg/L
7 | Room 114 North Island Sink West | HS2-7 | 10/25/2016 | .081 mg/L | Posted Non-Potable, Replace fixture, Retest
8 | Room 114 North Island Sink | HS2-8 | 10/25/2016 | .015 mg/L | Posted Non-Potable, Replace fixture, Retest
9 | Room 114 North Island Sink | HS2-9 | 10/25/2016 | .020 mg/L | Posted Non-Potable, Replace fixture, Retest
10 | Room 114 North Island Sink East | HS2-10 | 10/25/2016 | .32mg/L | Posted Non-Potable, Replace fixture, Retest
11 | Room 114 Teacher Sink | HS2-11 | 10/25/2016 | .027 mg/L | Posted Non-Potable, Replace fixture, Retest
12 | Room 114 South Sink | HS2-12 | 10/25/2016 | .031 mg/L | Posted Non-Potable, Replace fixture, Retest
13 | Room 115 Northeast Wall Sink | HS2-13 | 10/25/2016 | .0064 mg/L
14 | Room 115 Northwest Wall Sink | HS2-14 | 10/25/2016 | .012 mg/L
15 | Room 115 Window Sink Right | HS2-15 | 10/25/2016 | .0067 mg/L
16 | Room 115 Window Sink Center | HS2-16 | 10/25/2016 | .022 mg/L | Posted Non-Potable, Replace fixture, Retest
17 | Room 115 Window Sink Left | HS2-17 | 10/25/2016 | .076 mg/L | Posted Non-Potable, Replace fixture, Retest
18 | Room 115 Teacher Sink | HS2-18 | 10/25/2016 | .024 mg/L | Posted Non-Potable, Replace fixture, Retest
19 | Room 115 Storage Sink | HS2-19 | 10/25/2016 | .11 mg/L | Posted Non-Potable, Replace fixture, Retest
20 | Maintenance Break Room Sink | HS-5 | 4/11/2016 | <.0010 mg/L
21 | Maintenance Bath Hand Sink | HS2-21 | 10/25/2016 | <.0010 mg/L
22 | Faculty Mens Bath Hand Sink | HS2-22 | 10/25/2016 | .0031 mg/L
23 | Faculty Womens Bath Hand Sink | HS2-23 | 10/25/2016 | <.0010 mg/L
24 | Faculty Room Hand Sink | HS-6 | 4/11/2016 | <.0010 mg/L
25 | Maintenance Hall Water Fountain | HS-7 | 4/11/2016 | <.0010 mg/L
26 | Main Hall Custodial Sink | HS2-26 | 10/25/2016 | <.0010 mg/L
27 | Girls Locker Hand Sink Left | HS2-27 | 10/25/2016 | <.0010 mg/L
28 | Girls Locker Hand Sink Center | HS2-28 | 10/25/2016 | <.0010 mg/L
29 | Girls Locker Hand Sink Right | HS2-29 | 10/25/2016 | <.0010 mg/L
30 | Girls Locker Water Fountain | HS-18 | 4/11/2016 | <.0010 mg/L
31 | PE Office Bath Hand Sink | HS2-31 | 10/25/2016 | <.0010 mg/L
32 | Athletic Hall Custodial Sink | HS2-32 | 10/25/2016 | .052 mg/L | Posted Non-Potable, Replace fixture, Retest
33 | Athletic Hall Water Fountain Right | HS-19 | 4/11/2016 | <.0010 mg/L
34 | Athletic Hall Water Fountain Left | HS-20 | 4/11/2016 | <.0010 mg/L
35 | Mens Bath Hand Sink Left | HS2-35 | 10/25/2016 | <.0010 mg/L
36 | Mens Bath Hand Sink Center | HS2-36 | 10/25/2016 | <.0010 mg/L
37 | Mens Bath Hand Sink Right | HS2-37 | 10/25/2016 | <.0010 mg/L
38 | Womens Bath Hand Sink Right | HS2-38 | 10/25/2016 | .0013 mg/L
39 | Womens Bath Hand Sink Center | HS2-39 | 10/25/2016 | .0013 mg/L
40 | Womens Bath Hand Sink Left | HS2-40 | 10/25/2016 | .0018 mg/L
41 | Concession Sink | HS-24 | 4/11/2016 | .0042 mg/L
42 | Trainer Office Hand Sink | HS-23 | 4/11/2016 | .0033 mg/L
43 | Trainer Office Ice Machine | HS2-43 | 10/25/2016 | .015 mg/L | Posted Non-Potable, Replace fixture, Retest
44 | PE Office Bath Hand Sink Left | HS2-44 | 10/25/2016 | <.0010 mg/L
45 | PE Office Bath Hand Sink Right | HS2-45 | 10/25/2016 | .0011 mg/L
46 | Boys Locker Bath Hand Sink Left | HS2-46 | 10/25/2016 | .0012 mg/L
47 | Boys Locker Bath Hand Sink Center | HS2-47 | 10/25/2016 | <.0010 mg/L
48 | Boys Locker Bath Hand Sink Right | HS2-48 | 10/25/2016 | <.0010 mg/L
49 | Boys Locker Water Fountain | HS-21 | 4/11/2016 | <.0010 mg/L
50 | Boys Locker Team Room Water Fountain | HS-22 | 4/11/2016 | <.0010 mg/L
51 | Room 117 Hand Sink | HS-17 | 4/11/2016 | .0022 mg/L
52 | Room 117 Bath Hand Sink | HS2-52 | 10/25/2016 | .0011 mg/L
53 | Foreign Language Hall Water Fountain | HS-16 | 4/11/2016 | <.0010 mg/L
54 | Library Hall Custodial Sink | HS2-54 | 10/25/2016 | .0032 mg/L
55 | Library Hall Womens Bath Hand Sink | HS2-55 | 10/25/2016 | <.0010 mg/L
56 | Library Hall Mens Bath Hand Sink | HS2-56 | 10/25/2016 | <.0010 mg/L
57 | Library Bath Hand Sink | HS2-57 | 10/25/2016 | <.0010 mg/L
58 | Library Hand Sink | HS2-58 | 10/25/2016 | <.0010 mg/L
59 | Library Hall Water Fountain | HS-15 | 4/11/2016 | <.0010 mg/L
60 | Womens Bath Hand Sink Left | HS2-60 | 10/25/2016 | <.0010 mg/L
61 | Womens Bath Hand Sink Right | HS2-61 | 10/25/2016 | <.0010 mg/L
62 | Mens Bath Hand Sink Left | HS2-62 | 10/25/2016 | <.0010 mg/L
63 | Mens Bath Hand Sink Right | HS2-63 | 10/25/2016 | .0013 mg/L
64 | Senior Hall Water Fountain | HS-14 | 4/11/2016 | .0017 mg/L
65 | Nurses Office Bath Hand Sink | HS2-65 | 10/25/2016 | <.0010 mg/L
66 | Nurses Office Sink | HS-13 | 4/11/2016 | <.0010 mg/L
67 | Principal Office Bath Hand Sink | HS2-67 | 10/25/2016 | .0072 mg/L
68 | Womens Bath Hand Sink Left | HS2-68 | 10/25/2016 | .0098 mg/L
69 | Womens Bath Hand Sink Center | HS2-69 | 10/25/2016 | <.0010 mg/L
70 | Womens Bath Hand Sink Right | HS2-70 | 10/25/2016 | .0011 mg/L
71 | Main Office Water Fountain Left | HS-12 | 4/11/2016 | <.0010 mg/L
72 | Main Office Water Fountain Right | HS-11 | 4/11/2016 | <.0010 mg/L
73 | Mens Bath Hand Sink Right | HS2-73 | 10/25/2016 | .037 mg/L | Posted Non-Potable, Replace fixture, Retest
74 | Mens Bath Hand Sink Center | HS2-74 | 10/25/2016 | .0030 mg/L
75 | Mens Bath Hand Sink Left | HS2-75 | 10/25/2016 | .017 mg/L | Posted Non-Potable, Replace fixture, Retest
76 | Cafeteria Water Fountain Right | HS-10 | 4/11/2016 | <.0010 mg/L
77 | Cafeteria Water Fountain Left | HS-9 | 4/11/2016 | <.0010 mg/L
78 | Music Hall Water Fountain | HS-8 | 4/11/2016 | <.0010 mg/L
79 | Music Womens Bath Hand Sink Left | HS2-79 | 10/25/2016 | <.0010 mg/L
80 | Music Womens Bath Hand Sink Right | HS2-80 | 10/25/2016 | <.0010 mg/L
81 | Music Mens Bath Hand Sink Right | HS2-81 | 10/25/2016 | <.0010 mg/L
82 | Music Mens Bath Hand Sink Left | HS2-82 | 10/25/2016 | <.0010 mg/L
83 | Music Storage Hand Sink | HS2-83 | 10/25/2016 | .0059 mg/L
84 | Kitchen Ice Machine | HS2-84 | 10/25/2016 | .027 mg/L | Posted Non-Potable, Replace fixture, Retest
85 | Kitchen Wash Sink Left | HS-3 | 4/11/2016 | .0010 mg/L
86 | Kitchen Wash Sink Right | HS-4 | 4/11/2016 | .0015 mg/L
87 | Kitchen Hand Sink | HS2-87 | 10/25/2016 | .0013 mg/L
88 | Kitchen Island Sink | HS-2 | 4/11/2016 | .0011 mg/L
89 | Kitchen Cook Water Supply | HS2-89 | 10/25/2016 | .0015 mg/L
90 | Kitchen Wash Sink | HS-1 | 4/11/2016 | 0.0013 mg/L
91 | Kitchen Custodial Sink | HS2-91 | 10/25/2016 | <.0010 mg/L
92 | Kitchen Bath Hand Sink | HS2-92 | 10/25/2016 | <.0010 mg/L
93 | Room 232 Teacher Sink | HS2-93 | 10/25/2016 | .037 mg/L | Posted Non-Potable, Replace fixture, Retest
94 | Room 232 Island Sink Out | HS2-94 | 10/25/2016 | .16 mg/L | Posted Non-Potable, Replace fixture, Retest
95 | Room 232 Island Sink In | HS2-95 | 10/25/2016 | .037 mg/L | Posted Non-Potable, Replace fixture, Retest
96 | Room 232 Island Sink Out | HS2-96 | 10/25/2016 | .018 mg/L | Posted Non-Potable, Replace fixture, Retest
97 | Room 232 Island Sink In | HS2-97 | 10/25/2016 | .25 mg/L | Posted Non-Potable, Replace fixture, Retest
98 | Room 232 Island Sink Out | HS2-98 | 10/25/2016 | .020 mg/L | Posted Non-Potable, Replace fixture, Retest
99 | Room 232 Island Sink In | HS2-99 | 10/25/2016 | .014 mg/L
100 | Room 232 Island Sink Out | HS2-100 | 10/25/2016 | .0055 mg/L
101 | Room 232 Island Sink In | HS2-101 | 10/25/2016 | .0055 mg/L
102 | Room 232 Island Sink In | HS2-102 | 10/25/2016 | .038 mg/L | Posted Non-Potable, Replace fixture, Retest
103 | Room 232 Island Sink Out | HS2-103 | 10/25/2016 | .031 mg/L | Posted Non-Potable, Replace fixture, Retest
104 | Room 232 Island Sink In | HS2-104 | 10/25/2016 | .086 mg/L | Posted Non-Potable, Replace fixture, Retest
105 | Room 232 Island Sink Out | HS2-105 | 10/25/2016 | .072 mg/L | Posted Non-Potable, Replace fixture, Retest
106 | Room 234 Teacher Sink | HS2-106 | 10/25/2016 | .0070 mg/L
107 | Room 234 Island Sink Out | HS2-107 | 10/25/2016 | .019 mg/L | Posted Non-Potable, Replace fixture, Retest
108 | Room 234 Island Sink In | HS2-108 | 10/25/2016 | .031 mg/L | Posted Non-Potable, Replace fixture, Retest
109 | Room 234 Island Sink Out | Disconnected/Out of Service
110 | Room 234 Island Sink In | Disconnected/Out of Service
111 | Room 234 Island Sink Out | Disconnected/Out of Service
112 | Room 234 Island Sink In | Disconnected/Out of Service
113 | Room 234 Island Sink Out | Disconnected/Out of Service
114 | Room 234 Island Sink In | Disconnected/Out of Service
115 | Room 234 Island Sink Out | HS2-115 | 10/25/2016 | .053 mg/L | Posted Non-Potable, Replace fixture, Retest
116 | Room 234 Island Sink In | HS2-116 | 10/25/2016 | .036 mg/L | Posted Non-Potable, Replace fixture, Retest
117 | Room 234 Island Sink Out | HS2-117 | 10/25/2016 | .061 mg/L | Posted Non-Potable, Replace fixture, Retest
118 | Room 234 Island Sink In | HS2-118 | 10/25/2016 | .049 mg/L | Posted Non-Potable, Replace fixture, Retest
119 | Math Hall Water Fountain | HS-29 | 4/11/2016 | <.0010 mg/L
120 | Art/Business Hall Water Fountain | HS-28 | 4/11/2016 | <.0010 mg/L
121 | Art/Business Hall Custodial Sink | HS2-121 | 10/25/2016 | .0050 mg/L
122 | Room 231 Island Sink Window | HS2-122 | 10/25/2016 | .0028 mg/L
123 | Room 231 Island Sink Hall | HS2-123 | 10/25/2016 | .0021 mg/L
124 | Room 233 Island Sink Window | HS2-124 | 10/25/2016 | .0029 mg/L
125 | Room 233 Island Sink Hall | HS2-125 | 10/25/2016 | <.0010 mg/L
126 | Room 233 Sink | HS2-126 | 10/25/2016 | .0018 mg/L
127 | Dark Room Sink Right | HS2-127 | 10/25/2016 | <.0010 mg/L
128 | Dark Room Sink Center | HS2-128 | 10/25/2016 | .0052 mg/L
129 | Dark Room Sink Left | HS2-129 | 10/25/2016 | .0048 mg/L
130 | Sophomore Hall Water Fountain | HS-27 | 4/11/2016 | <.0010 mg/L
131 | 2nd Floor Girls Bath Hand Sink Left | HS2-131 | 10/25/2016 | .0076 mg/L
132 | 2nd Floor Girls Bath Hand Sink Center | HS2-132 | 10/25/2016 | .0055 mg/L
133 | 2nd Floor Girls Bath Hand Sink Right | HS2-133 | 10/25/2016 | .0033 mg/L
134 | 2nd Floor Bath Water Fountain Left | HS-26 | 4/11/2016 | <.0010 mg/L
135 | 2nd Floor Bath Water Fountain Right | HS-25 | 4/11/2016 | .0011 mg/L
136 | 2nd Floor Boys Bath Hand Sink Right | HS2-136 | 10/25/2016 | .0015 mg/L
137 | 2nd Floor Boys Bath Hand Sink Center | HS2-137 | 10/25/2016 | .0036 mg/L
138 | 2nd Floor Boys Bath Hand Sink Left | HS2-138 | 10/25/2016 | .0014 mg/L
139 | 2nd Floor Womens Faculty Bath Sink | HS2-139 | 10/25/2016 | .0012 mg/L
140 | 2nd Floor Mens Faculty Bath Sink | HS2-140 | 10/25/2016 | <.0010 mg/L
141 | 2nd Floor Music Hall Water Fountain | HS-30 | 4/11/2016 | <.0010 mg/L
142 | Room 213 Teacher Sink | HS2-142 | 10/25/2016 | .016 mg/L | Posted Non-Potable, Replace fixture, Retest
143 | Room 213 East Hand Sink | HS2-143 | 10/25/2016 | .0066 mg/L
144 | Room 213 Island Sink East | HS2-144 | 10/25/2016 | .017 mg/L | Posted Non-Potable, Replace fixture, Retest
145 | Room 213 Island Sink West | HS2-145 | 10/25/2016 | .0091 mg/L
146 | Room 213 West Sink Right | HS2-146 | 10/25/2016 | .0043 mg/L
147 | Room 213 West Sink Left | HS2-147 | 10/25/2016 | .013 mg/L
148 | Room 213/211 South Sink | HS2-148 | 10/25/2016 | .18 mg/L | Posted Non-Potable, Replace fixture, Retest
149 | Room 213/211 East Sink | HS2-149 | 10/25/2016 | .034 mg/L | Posted Non-Potable, Replace fixture, Retest
150 | Room 211 East Sink Right | HS2-150 | 10/25/2016 | .0098 mg/L
151 | Room 211 East Sink Left | HS2-151 | 10/25/2016 | .0053 mg/L
152 | Room 211 Island Sink East | HS2-152 | 10/25/2016 | .13 mg/L | Posted Non-Potable, Replace fixture, Retest
153 | Room 211 Island Sink West | HS2-153 | 10/25/2016 | .020 mg/L | Posted Non-Potable, Replace fixture, Retest
154 | Room 211 West Sink | HS2-154 | 10/25/2016 | .040 mg/L | Posted Non-Potable, Replace fixture, Retest
155 | Room 211 Teacher Sink | HS2-155 | 10/25/2016 | .83 mg/L | Posted Non-Potable, Replace fixture, Retest
156 | Technology Hall Water Fountain | HS-31 | 4/11/2016 | .0013 mg/L
157 | Room 214 Teacher Sink | HS2-157 | 10/25/2016 | <.0010 mg/L
158 | Room 214 Window Sink Left | HS2-158 | 10/25/2016 | <.0010 mg/L
159 | Room 214 Window Sink Left/Center | HS2-159 | 10/25/2016 | .0052 mg/L
160 | Room 214 Window Sink Right/Center | HS2-160 | 10/25/2016 | <.0010 mg/L
161 | Room 214 Window Sink Right | HS2-161 | 10/25/2016 | .032 mg/L | Posted Non-Potable, Replace fixture, Retest
162 | Science Hall Custodial Closet | HS2-162 | 10/25/2016 | .042 mg/L | Posted Non-Potable, Replace fixture, Retest
163 | Room 210 Teacher Sink | HS2-163 | 10/25/2016 | .030 mg/L | Posted Non-Potable, Replace fixture, Retest
164 | Room 210 Island Sink Out | Disconnected/Out of Service
165 | Room 210 Island Sink In | Disconnected/Out of Service
166 | Room 210 Island Sink Out | Disconnected/Out of Service
167 | Room 210 Island Sink In | Disconnected/Out of Service
168 | Room 210 Island Sink Out | Disconnected/Out of Service
169 | Room 210 Island Sink In | Disconnected/Out of Service
170 | Room 210 Island Sink Out | Disconnected/Out of Service
171 | Room 210 Island Sink In | Disconnected/Out of Service
172 | Room 210 Island Sink Out | Disconnected/Out of Service
173 | Room 210 Island Sink In | Disconnected/Out of Service
174 | Room 210 Island Sink Out | Disconnected/Out of Service
175 | Room 210 Island Sink In | Disconnected/Out of Service
176 | Room 210 Island Sink Out | Disconnected/Out of Service
177 | Room 210 Island Sink In | Disconnected/Out of Service
178 | Room 210/212 Sink South | HS2-178 | 10/25/2016 | .10 mg/L | Posted Non-Potable, Replace fixture, Retest
179 | Room 210/212 Sink East | HS2-179 | 10/25/2016 | .048 mg/L | Posted Non-Potable, Replace fixture, Retest
180 | Room 212 Teacher Sink | Disconnected/Out of Service
181 | Room 212 West Sink | HS2-181 | 10/25/2016 | .0024 mg/L
182 | Room 212 Island Sink Hall | Disconnected/Out of Service
183 | Room 212 Island Sink Window | Disconnected/Out of Service
184 | Room 212 Island Sink Hall | Disconnected/Out of Service
185 | Room 212 Island Sink Window | Disconnected/Out of Service
186 | Room 212 Island Sink Hall | Disconnected/Out of Service
187 | Room 212 Island Sink Window | Disconnected/Out of Service
188 | Room 212 East Sink Right | HS2-188 | 10/25/2016 | .0041 mg/L
189 | Room 212 East Sink Left | HS2-189 | 10/25/2016 | .011 mg/L
190 | Room 212 Island Sink East | HS2-190 | 10/25/2016 | .71 mg/L
191 | Room 212 Island Sink West | HS2-191 | 10/25/2016 | .099 mg/L
192 | Concession Hose Bib | HS-32 | 4/11/2016 | .02 mg/L | Checked supply lines/cleaned aerators/flushed system | HS-1 | 7/22/2016 | .0083 mg/L
193 | Concession Sink | HS-33 | 4/11/2016 | .02 mg/L | Checked supply lines/cleaned aerators/flushed system | HS-2 | 7/22/2016 | .0022 mg/L
194 | Concession Mens Bath Hand Sink | HS2-194 | 10/25/2016 | <.0010 mg/L
195 | Concession Womens Bath Hand Sink | HS2-195 | 10/25/2016 | <.0010 mg/L
196 | Serving Line Coffee Maker | HS2-196 | 10/25/2016 | .0046 mg/L
197 | Room 115 Sink | HS2-197 | 10/25/2016 | .32 mg/L | Posted Non-Potable, Replace fixture, Retest

## Lake Street
Location Number | Description | Sample # | Sample Date | Results | Remediation | Retest Sample # | Retest Date | Retest Results
1 | Gym Hall Water Fountain Left | LS-3 | 5/4/2016 | .0012 mg/L
2 | Gym Hall Water Fountain Right | LS-4 | 5/4/2016 | .0014 mg/L
3 | Boys Gang Bath Hand Sink Left | LS2-3 | 10/25/2016 | .0048 mg/L
4 | Boys Gang Bath Hand Sink Center | LS2-4 | 10/25/2016 | .0020 mg/L
5 | Boys Gang Bath Hand Sink Right | LS2-5 | 10/25/2016 | .0038 mg/L
6 | Girls Gang Bath Hand Sink Left | LS2-6 | 10/25/2016 | .0092 mg/L
7 | Girls Gang Bath Hand Sink Center | LS2-7 | 10/25/2016 | .0056 mg/L
8 | Girls Gang Bath Hand Sink Right | LS2-8 | 10/25/2016 | .0032 mg/L
9 | Boys Locker Water Fountain | LS-1 | 5/4/2016 | .0091 mg/L | Disconnected power and water supply to fountain. No longer in service.
10 | Boys Locker Bath Hand Sink Right | LS2-10 | 10/25/2016 | .0079 mg/L
11 | Boys Locker Bath Hand Sink Left | LS2-11 | 10/25/2016 | .018 mg/L | Posted Non-Potable, Replace fixture, Retest
12 | Girls Locker Water Fountain | LS-2 | 5/4/2016 | .018 mg/L | Disconnected power and water supply to fountain. No longer in service.
13 | Girls Locker Bath Hand Sink | LS2-13 | 10/25/2016 | .036 mg/L | Posted Non-Potable, Replace fixture, Retest

## Transportation
Location Number | Description | Sample # | Sample Date | Results | Remediation | Retest Sample # | Retest Date | Retest Results
1 | Hall Water Fountain Right | BG-1 | 5/4/2016 | <.0010 mg/L
2 | Hall Water Fountain Left | BG-2 | 5/4/2016 | <.0010 mg/L
3 | Drive Break Room Hand Sink | BG-3 | 5/4/2016 | <.0010 mg/L
4 | Mechanic Break Room Hand Sink | BG-4 | 5/4/2016 | <.0010 mg/L

## Maintenance
Location Number | Description | Sample # | Sample Date | Results | Remediation | Retest Sample # | Retest Date | Retest Results
1 | First Floor Break Room Hand Sink | MT-1 | 5/4/2016 | <.0010 mg/L
2 | Water Fountain | MT-2 | 5/4/2016 | <.0010 mg/L